FILT&SWAP Inline filter

0.2µm microfiltration

Reference: AT50671

Specification description

FILT&SWAP inline anti-Legionella filter 0.2µm.

Microfiltration: Retains all bacteria and other particles larger than 0.2µm.

Filter cartridge can be replaced without changing the filter body.

Membrane surface area: 19.6” (0.5m²).

Capacity: 3,959.5 Gallons (18,000L).

Maximum lifespan: 6 months.

Filtration flow rate: 2.37 gpm (9 lpm) with integrated flow restrictor; 3.7 gpm (14 lpm) without flow restrictor at 45 psi (3 bar).

Materials: Body and filtration cartridge made of polypropylene. Filter cartridge plastic components made of ABS.

Temperature: 39 - 100°F (4 - 38°C).

Operating pressure: 7 - 145 psi (0.5 - 10 bar).

Connection type: 3/8" compression or NPT.

Compatible with and resistant to chemical shocks (active chlorine levels up to 100 ppm for 1 hour (cumulative total) and thermal shocks (158°F / 70°C for 30 minutes).